## Slide 1
Choosing the Right Boiler
What is the Heat Load of the Home or Building you are Trying to Heat
Is the Connected Radiation Less then or Greater than the Heat Load
What is the System Made up of (Baseboard, Cast Iron Radiators Air Handlers)
Is the Boiler a Steam Boiler
What is the connected Radiation?
Questions that Need to be asked before Choosing the Boiler

## Slide 2
Choosing the Right Boiler
Question: If the Buildings or Home Heat Load is Greater then the Connected Radiation then
Is it a Good Application for a Condensing Boiler.
Question: If the Connected Radiation Is Greater then the Heat Load then is this a Good Application For a Condensing Boiler.

## Slide 3
Choosing the Right Boiler
Did You Know
That a Condensing boilers efficiency are based on 140 degree supply water Temperature
and 120 degree return water temperature and that the higher the supply
and return water temperature rises the lower the efficiency.

## Slide 4
Choosing the Right Boiler
Did You Know
That the Highest Efficiency System for a Modcon is
Geothermal, Radiant or a Snowmelt system.

## Slide 5
Choosing the Right Boiler
Choosing the right boiler starts with the heat load for the structure. Once the
Heat load has been calculated then the contractor will need to measure the
connected radiation. The connected radiation needs to be equal or greater
then the heat load calculation for a modcon to heat the structure properly.
If the connected radiation BTU’s is lower then the boilers maximum output BTU’s
then the structure is not the right application for a modcon boiler.

## Slide 6
Choosing the Right Boiler
If there is no way to increase the connected radiation by adding
baseboard or a radiator then the better alternative would be a cast iron boiler.
With a cast iron boiler you can increase the boilers supply water temperature to overcome the lower BTU’s of the connected radiation.

## Slide 7
Choosing the Right Boiler
The maximum supply water temperature for a modcon boiler is 185 degrees F
The maximum supply water temperature for a cast iron boiler is 220 degrees F
A majority of all hydronic systems are designed around a 20 degree Delta T
Radiant heating is designed at a 8 – 12 degree Delta T

## Slide 8
Near Boiler Piping
Near boiler piping is a problem primarily with modcon boilers. The pipe size from the boiler is to supply water at a calculated GPM and foot of head just for the boiler heat exchanger.
The near boiler piping size (GPM/BTU’s) needs to equal the BTU’s for the output for the boiler. This is the same for cast ion boilers.

## Slide 9
Near Boiler Piping
How do we get to the numbers you might ask
Simple
BTUH
 X 500

## Slide 10
Near Boiler Piping
BTUH – Is the Output of the Boiler
 - Is how much Temperature is Lost
500 - 1 Pound of Water 1 Degree in 1 Hour

## Slide 11
Near Boiler Piping
500 is a shortcut representing the weight of one gallon of water (8.33 pounds), times 60 minutes in an hour, times the specific heat characteristic of the fluid (1 for 100 percent water). It takes 1 Btu to raise the temperature of 1 pound of water 1 degree in 1 hour.
8.33 x 60 x 1 = 499.8 (500)
What the Numbers Mean

## Slide 12
GPM = Btuh/ ΔT X 500
GPM = 70,500 / 20 X 500
GPM = 70,500/10,000
GPM = 7.1
Near Boiler Piping

## Slide 13
Near Boiler Piping
Pressure is measured in Pounds Per Square Inch (PSI). One column of water 2.31 feet, or 28 inches high will have a pressure of 1 PSI at the bottom.
1 PSI = 2.31 Foot of head
Converting PSI to Head Loss

## Slide 14
Near Boiler Piping
Zone Head Loss
What is Head Loss
Head Loss is the resistance in a piping circuit. Fittings and Valves produce pressure drop in a system equivalent to a few feet of pipe. To accommodate basic fittings and valves multiply the total length of pipe by 1.5.

## Slide 15
Near Boiler Piping
Zone Head Loss
Once we know the total length multiplied by 1.5 then you take that number and
Multiply by .04. (Pipe Friction Value)
.04 is four foot of head per 100 feet of copper pipe The Head number applies
As long the right pipe size is chosen for 2-4 feet per second.

## Slide 16
Near Boiler Piping
Zone Head Loss
If the zone is 100 foot this is what the math would look like.
Head = 100 foot X 1.5 X .04 = 6 foot of Head

## Slide 17
Near Boiler Piping and System Piping
Piping Sizing Guidelines
Pipe Size Max Flow BTU’s
½ in. 2 20,000
3/4 in. 4 40,000
1 in. 8 80,000
1 ¼ 14 140,000
1 ½ 22 220,000
45 450,000
130 1,300,000
300 3,000,000
6 850 8,500,000

## Slide 18
Near Boiler Piping and System Piping
Piping Sizing Guidelines PEX
Tube Size Max Flow BTU’s
3/8 in. 1.2 12,000
½ in. 2 20,000
5/8 in. 4 40,000
¾ in. 6 60,000
1 in. 10 100,000

## Slide 19
Questions ?
Thank you!